## Cover
5JEM2-TALLGRASS UNIT 2
MODULE NO.MD-3.2
TP No. CT9-TP-MD-3.2-2

## Sheet1
PRESSURE TEST INFORMATION
Client |  | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. |  | Report No. |  | CT9-TP-MD-3.2-2
Project Name |  | 5JEM2-TALLGRASS UNIT 2 |  | Project No. |  | CT9
Block/Module No. |  | MD-3.2 |  | Location |  | On Module
Piping System |  | 24A0A |  | Test Package No. |  | CT9-TP-MD-3.2-2
Piping Name |  | INSTRUMENT AIR PIPING |  | P&ID No. |  | N01-PID-QFF-00-02
Test Medium |  | Nitrogen (N2) |  | Insulation Spec. |  | N/A
Design Pressure |  | 1.03 / 10.3 | Mpag / bar | Insulation Thk. |  | N/A
Design Temp. |  | 60 | ˚C
Fluid Code |  | IA, INSTRUMENT AIR
Pipe Material |  | A312-TP304
Test Pressure |  | 12.36 | bar(g.)
Holding Time |  | 10 | min.
0 | ISSUED FOR TEST |  |  | 2026-10-27 | TAWEESAK J. | PUNLOP M. | MINU LEE
REV. | DESCRIPTION |  |  | DATE | PREPARED BY | REVIEW BY | APPROVED BY
REVISION NOTE
PREPARED BY |  |  | TEST/INSPECTOR BY |  | TESTING APPROVED BY
Taweesak J.
(BJCHI ENGINEERING) |  |  | (BJCHI QC/INSPECTOR) |  | (CIMTAS REPRESENTIVE)
2026-10-27 |  |  | / / |  | / /
------------------------------------------------------- |  |  | ---------------------------------------------------------------- |  | --------------------------------------------------------------------
DATE |  |  | DATE |  | DATE

## Sheet2
TEST PACK CONTENT CHECK LIST
Project Name |  | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description |  | CONTENT LIST | Module Name | MD-3.2
System Name |  | INSTRUMENT AIR PIPING | Piping System | 24A0A
SECTION | CONTENT LIST |  |  | VERIFY
1 | Revalant P&ID |  |  | YES | N/A
2 | Line list |  |  | YES | N/A
3 | General Arrangement/Isometric Drawing/Pipe Support |  |  | YES | N/A
4 | Piping welding tracebility recoed (welding history sheet report) |  |  | YES | N/A
5 | NDE report |  |  | YES | N/A
6 | Inspection recoed of flange joint assembly & sprial wound gasket tightening |  |  | YES | N/A
7 | Dimension verification record (A3) |  |  | YES | N/A
8 | Piping Pneumatic/hydro-test preparation checklist (Pre-test checklist) |  |  | YES | N/A
9 | Pressure gauge calibration certification |  |  | YES | N/A
10 | Pressure-test report |  |  | YES | N/A
11 | Paint inspection report (TOUCH-UP) |  |  | YES | N/A
12 | Insulation check list |  |  | YES | N/A
13 | Piping cleaning and verification record |  |  | YES | N/A
14 | Piping restoration checklist |  |  | YES | N/A
15 | Punch list |  |  | YES | N/A

## SECTION #1
SECTION #1
Project Name |  | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description |  | Revalant P&ID | Module Name | MD-3.2
System Name |  | INSTRUMENT AIR PIPING | Piping System | 24A0A
N/A

## SECTION #2
SECTION #2
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Line List | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## ISO INDEX
TEST PACK ISOMETRIC INDEX
Project Name |  |  | 5JEM2-TALLGRASS UNIT 2 | [14 empty] | Test Package No. |  |  | CT9-TP-MD-3.2-2
Description |  |  | Line List | [14 empty] | Module Name | Module Name |  | MD-3.2
System Name | System Name |  | INSTRUMENT AIR PIPING | [14 empty] | Piping System | System Name |  | 24A0A
No. |  | ISOMETRIC DRAWING |  |  |  | PID DRAWING |  |  | MODULE No. | LINE No. | SPOOL No. | FLUID | DESIGN PRESSURE (Mpag / bar) | DESIGN TEMPERATURE (˚C) | TEST PRESSURE (bar) | TEST TYPE | MATERIAL | INSULATION |  |  | PIPE NPD (IN) | REMARK
|  | DRAWING No. |  | SHT. | REV. | DRAWING No. | SHT. | REV. | [9 empty] | SPEC |  | THK(MM)
1 |  | N05-003580 |  | 3 OF 5 | 0 | N01-PID-QFF-00-02 | - | - | MD-3.2 | **QFF11BR621 | **24A0A-66 | IA, INSTRUMENT AIR | 1.03 / 10.3 | 60 | 12.36 | P | A312-TP304 | N/A |  | N/A | 1.5
2 |  | N05-003580 |  | 3 OF 5 | 0 | N01-PID-QFF-00-02 | - | - | MD-3.2 | **QFF11BR621 | **24A0A-68 | IA, INSTRUMENT AIR | 1.03 / 10.3 | 60 | 12.36 | P | A312-TP304 | N/A |  | N/A | 1.5

## SECTION #3
SECTION #3
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | General Arrangement / Isometric Drawing / Pipe Support | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #4
SECTION #4
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Piping Welding Traceability Record (WHS) | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #5
SECTION #5
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | NDE Report | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #6
SECTION #6
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Inspection Record of Flange Joint Assembly & Spiral Would Gasket | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #7
SECTION #7
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Dimension Verification Record (A3) | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #8
SECTION #8
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Piping Pneumatic / Hydro Test Prepration Check List (Pre-test Check List) | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## Sheet5
PRESSURE TEST PACK CHECKLIST
CLIENT: |  | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | [8 empty] | REPORT NO. |  | CT9-TP-MD-3.2-2
PROJECT NO: |  | CT9 | [8 empty] | PAGES: |  | 1 of 1
PROJECT TITLE: |  | 5JEM2-TALLGRASS UNIT 2 | [8 empty] | INSPC' DATE: |  | 2026-01-08
BLOCK/MODULE NAME/NO: |  | MD-3.2 | [8 empty] | LOCATION: |  | BJCHI
PRESSURE TEST PACKAGE NO: |  | CT9-TP-MD-3.2-2 | [8 empty] | TEST STAGE:
PRESSURE TEST METHOD |  | HYDROSTATIC TEST PNEUMATIC TEST | [8 empty] | ISOMETRIC NO: |  | N05-003580 Rev.0
DOCUMENT CHECKLIST | [7 empty] | TEST PREPRATION CHECKLIST
ITEM NO. | DOCUMENT DESCRIPTION |  |  |  | STATUS |  |  | ITEM NO. | TEST ITEM DESCRIPTION |  |  |  | STATUS |  |  | REMARKS
[5 empty] | YES | NO | N/A | [5 empty] | YES | NO | N/A
1 | Test Pack Line List |  |  |  | / |  |  | 1 | Check correct gaskets & bolts are fitted at all mechaniccal joints
2 | Drawing List and Correct Revision No's |  |  |  | / |  |  | 2 | Check Fitting are correct rating to specification |  |  |  | /
3 | P&ID Drawing and P&ID List | [5 empty] | / | 3 | Check all Flanged has correctly alligned
4 | Flushing Test Report | [5 empty] | / | 4 | Check all Vent and Drains are correctly installed | [5 empty] | /
5 | Punch List |  |  |  | / |  |  | 5 | Check correct Valves have been fitted and are complete |  |  |  | /
6 | Pressure and Temperature Gauge Calibration Certs. |  |  |  | / |  |  | 6 | Check correct Flow through Valves and In Line Devices |  |  |  | /
7 | NDT and Inspection Release Note (IRN) |  |  |  | / |  |  | 7 | Check that all Instrument Connection are correctly Installed | [5 empty] | /
8 | Weld History Sheet completed |  |  |  | / |  |  | 8 | Check all Pipe Support are fitted and complete |  |  |  | /
9 | Test Medium Certificate | [5 empty] | / | 9 | Check that all pipe work is adequately supported for test |  |  |  | /
10 | Site Technical Queries | [5 empty] | / | 10 | Check pressure and temp. gages are installed at correct location |  |  |  | /
11 | Special Instruction | [5 empty] | / | 11 | Check that temperature recorder and pressure recorder installed | [5 empty] | /
12 | Pressure Testing procedure |  |  |  | / |  |  | 12 | Check Safety Barricade and Warning Signs has installed |  |  |  | /
13 | Pressure Test Chart Form approved | [5 empty] | / | 13 | Check Work permit has been issued by BJCHI HSE Department |  |  |  | /
14 | Pressure Testing Report Form |  |  |  | /
15 | Mechanical Equipment's List Approved by Engineering | [5 empty] | /
16 | Record of all Fittings are available | [5 empty] | /
17 | Check PWHT, PMI and Ferrite Test reports are available | [5 empty] | /
Note: When above Status indicates "NO" a punch list must be raised by QC and Pressure Test shall not be proceed.
REVIEW & WITNESS.
COMPLETED BY. |  |  | BJCHI. | [6 empty] | CIMTAS. |  | REPRESENTATIVE.
NAME : | Mr.Cholachai J. |  | NAME : | Mr.Cholachai J. | [5 empty] | NAME : |  | NAME :
POSITION : |  |  | POSITION : | [6 empty] | POSITION : |  | POSITION :
SIGNATURE : |  |  | SIGNATURE : | [6 empty] | SIGNATURE : |  | SIGNATURE :
DATE : | 2026-01-08 |  | DATE : | 2026-01-08 | [5 empty] | DATE : |  | DATE :

## SECTION #9
SECTION #9
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Pressure Gauge Calibration Certification | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #10
SECTION #10
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Pressure Test Report | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #11
SECTION #11
Project Name |  | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description |  | Paint Inspection Report (TOUCH-UP) | Module Name | MD-3.2
System Name |  | INSTRUMENT AIR PIPING | Piping System | 24A0A
N/A

## SECTION #12
SECTION #12
Project Name |  | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description |  | Insulation Check List | Module Name | MD-3.2
System Name |  | INSTRUMENT AIR PIPING | Piping System | 24A0A
N/A

## SECTION #13
SECTION #13
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Piping Clening and Verification Record | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## SECTION #14
SECTION #14
Project Name |  | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description |  | Piping Restoration Check List | Module Name | MD-3.2
System Name |  | INSTRUMENT AIR PIPING | Piping System | 24A0A
N/A

## SECTION #15
SECTION #15
Project Name | 5JEM2-TALLGRASS UNIT 2 | Test Package No. | CT9-TP-MD-3.2-2
Description | Punch List | Module Name | MD-3.2
System Name | INSTRUMENT AIR PIPING | Piping System | 24A0A

## Sheet6
PROCESS PUNCH-LIST
CLIENT: |  | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | [7 empty] | REPORT NO. |  |  |  | CT9-TP-MD-3.2-2
PROJECT NO: |  | CT9 | [7 empty] | PAGES: |  |  |  | 1 of 1
PROJECT NAME: |  | 5JEM2-TALLGRASS UNIT 2 | [7 empty] | INSPC' DATE: |  |  |  | 2026-01-08
BLOCK/MODULE NAME/NO: |  | MD-3.2 | [7 empty] | LOCATION: |  |  |  | BJCHI
PROCESS DISCIPLINE |  | PIPING | [7 empty] | TEST STAGE:
ITEM NO. | DRAWING NO. | PUNCH-LIST DESCRIPTION |  |  |  |  | CATEGORY "A" "B" | STATUS OPEN / CLOSED | PUNCH CLOSING ACTION AND VERIFICATION | [5 empty] | REMARKS
[9 empty] | PROD SUP. |  | QCI |  | CLIENT REP.
PUNCH-LIST DEFINITION OF TERMS
"A" : Any subsequent operation or process cannot be performed until punch is closed. | [6 empty] | "B" : Subsequent operation can be proceeding with discretion of project manager
REVIEW & WITNESS.
COMPLETED BY. |  |  | BJCHI. |  |  | CIMTAS. | [5 empty] | REPRESENTATIVE.
NAME : | Mr. Cholachai J. |  | NAME : | Mr.Cholachai J. |  | NAME : | [5 empty] | NAME :
POSITION : |  |  | POSITION : |  |  | POSITION : | [5 empty] | POSITION :
SIGNATURE : |  |  | SIGNATURE : |  |  | SIGNATURE : | [5 empty] | SIGNATURE :
DATE : | 2026-01-09 |  | DATE : | 2026-01-09 |  | DATE : | [5 empty] | DATE :