## Pressure_Test_Joints
Project_No | Module | Unit | Weld_Map_No | Item | Joint | Rev | Spool | Type | P_No | Size | DB | Film | Sch | Thk | Type1 | Type2 | Material | Description1 | Description2 | WPS_No | Process1 | FIT UP | WELDING | VISUAL | NDT | PT | Report No | RT | RT 1 | NDT Status | TP no. | Service | Test pressure (Bar) | Third party Inspection | Line check before pressure test | Pressure test | Remark
CT3 | A1-3 | 1 | G1-S4464 | 1 | S-9 | 1 | DSA-250B | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A182 F304 | 304 | Pipe | Full coupling | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 | 2025-01-26 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-A1-3-002 | Seal air | 6.72 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-3 | 1 | G1-S4466 | 1 | S-18 | 1 | DIA-250A | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-01-28 00:00:00 | 2025-01-28 00:00:00 | 2025-01-28 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-3 | 1 | G1-S4467 | 1 | S-10 | 1 | DIA-251B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 | 2025-01-26 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-3 | 1 | G1-S4467 | 1 | S-14 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 | 2025-01-26 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-3 | 1 | G1-S4467 | 1 | S-29 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-01-28 00:00:00 | 2025-01-28 00:00:00 | 2025-01-28 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-3 | 1 | G1-S4474 | 1 | S-12 | 1 | DLOR-250A | BW | 1 | L | 10 | 3 | S40 | 9.27 | A106 Gr.B | A106 Gr.B | CS | Pipe | Pipe | BJC-G-1/1-154 | GTAW | 2025-01-20 00:00:00 | 2025-01-21 00:00:00 | 2025-01-21 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-A1-3-003 | Lube oil return | 1.2 | No | 2025-01-27 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A1-4 | 1 | G1-S4023 | 1 | S-5 | 2 | DFBA-275-1 | BW | 1 | S | 3 | 3 | S40 | 5.49 | A106 Gr.B | A234 WPB | CS | Pipe | Tee | BJC-G-1/1-154 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 |  | - | - | ACC | - | Clear | CT3-TP-A1-4-001 | Filter bleed air | 1.2/33.6 | No | 2025-03-10 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A3-3 | 1 | G1-S4506 | 1 | S-8 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-01-28 00:00:00 | 2025-02-01 00:00:00 | 2025-02-01 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 | No | 2025-01-27 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | A3-3 | 1 | G1-S4506 | 1 | S-9 | 2 | DGSA-400-1 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-01-28 00:00:00 | 2025-02-01 00:00:00 | 2025-02-01 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 | No | 2025-01-27 00:00:00 | 2025-03-10 00:00:00 | N/A
CT3 | C2-1 | 1 | G1-S4010 | 1 | S-14 | 1 | DIA-525B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-01-20 00:00:00 | 2025-01-20 00:00:00 | 2025-01-21 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-C2-1-001 | Instrument air | 12 | No | 2025-03-15 00:00:00 | 2025-03-15 00:00:00 | N/A
CT3 | D1-2 | 1 | G1-S4530 | 1 | seal weld 1 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 | No | Cancel | Cancel | N/A
CT3 | D1-2 | 1 | G1-S4530 | 1 | seal weld 2 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 | No | Cancel | Cancel | N/A
CT3 | D1-2 | 1 | G1-S4531 | 1 | S-6 | 2 | DSA-625 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 | No | 2025-03-15 00:00:00 | 2025-03-15 00:00:00 | N/A
CT3 | D1-2 | 1 | G1-S4531 | 1 | S-7 | 2 | DSA-625-1 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 | No | 2025-03-15 00:00:00 | 2025-03-15 00:00:00 | N/A
CT3 | D1-2 | 1 | G1-S4531 | 1 | S-15 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 | No | 2025-03-15 00:00:00 | 2025-03-15 00:00:00 | N/A
CT3 | D1-2 | 1 | G1-S4531 | 1 | S-16 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 | No | 2025-03-15 00:00:00 | 2025-03-15 00:00:00 | N/A
CT3 | D2-1 | 1 | G1-S4087 | 1 | S-6 | 1 | DG-657A | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-22 00:00:00 | 2025-01-22 00:00:00 | 2025-01-23 00:00:00 |  | - | RT-D2-1-001R2 | REJ | ACC | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-1 | 1 | G1-S4087 | 1 | S-7 | 1 | DG-657B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-21 00:00:00 | 2025-01-21 00:00:00 | 2025-01-22 00:00:00 |  | - | RT-D2-1-001R1 | REJ | ACC | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4091 | 1 | S-1 | 4 | DG-675A | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-01-29 00:00:00 | 2035-01-30 00:00:00 | 2035-01-30 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4091 | 1 | S-15 | 4 | DG-675A | FW | 8 | N/A | 10 | N/A | S80 | 12.70 | A312 TP304-S | A240 304 | 304 | Pipe | Plate | BJC-G-8/8-353 | GTAW | 2025-02-28 00:00:00 | 2025-02-28 00:00:00 | 2025-03-01 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4092 | 1 | S-10 | 3 | DG-676C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-31 00:00:00 | 2025-01-31 00:00:00 | 2025-01-31 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4092 | 1 | S-16 | 3 | DG-676AB | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-01-29 00:00:00 | 2025-01-30 00:00:00 | 2025-01-30 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4092 | 1 | S-6 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-01-25 00:00:00 | 2025-01-25 00:00:00 | 2025-01-26 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4092 | 1 | S-9 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-31 00:00:00 | 2025-01-31 00:00:00 | 2025-01-31 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4094 | 1 | S-10 | 3 | DG-678B | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4094 | 1 | S-19 | 3 | DG-678A | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D2-2 | 1 | G1-S4094 | 1 | S-30 | 3 | DG-678A | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-01-24 00:00:00 | 2025-01-24 00:00:00 | 2025-01-25 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | S-11 | 3 | DGSA-700AC | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-01-28 00:00:00 | 2025-02-01 00:00:00 | 2025-02-01 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | S-12 | 3 | DGSA-700B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-01-28 00:00:00 | 2025-02-01 00:00:00 | 2025-02-01 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | S-12RW | 3 | DGSA-700B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-02-24 00:00:00 | 2025-02-24 00:00:00 | 2025-02-24 00:00:00 | 2025-02-24 00:00:00 | - |  | ACC |  | Clear | CT3-TP-D3-1-001 | Fuel gas |  |  | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | RW=Re-weld for adjust alignment
CT3 | D3-1 | 1 | G1-S4100 | 1 | S-4 | 3 | DGSA-700D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-30 00:00:00 | 2025-01-30 00:00:00 | 2025-02-01 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | S-5 | 3 | DGSA-700C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-30 00:00:00 | 2025-01-30 00:00:00 | 2025-02-01 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | seal weld 1 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-02-28 00:00:00 | 2025-02-28 00:00:00 | 2025-03-01 00:00:00 | 2025-03-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | seal weld 2 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-02-28 00:00:00 | 2025-02-28 00:00:00 | 2025-03-01 00:00:00 | 2025-03-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-1 | 1 | G1-S4100 | 1 | seal weld 3 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-02-28 00:00:00 | 2025-02-28 00:00:00 | 2025-03-01 00:00:00 | 2025-03-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-10 | 5 | DFPA-710E | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-16 | 5 | DFPA-710BD | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | - | RT-D3-2-0003R1 | REJ | ACC | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-17 | 5 | DFPA-710C | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-3 | 5 | DFPA-710A | BW | 8 | S | 4 | 3 | S40 | 6.02 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | - | RT-D3-2-0001RS | RS | ACC | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-4 | 5 | DFPA-710D | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | - |  | ACC |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | D3-2 | 1 | G1-S4104 | 1 | S-9 | 5 | DFPA-710D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-01-23 00:00:00 | 2025-01-23 00:00:00 | 2025-01-24 00:00:00 |  | ACC | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 | Yes | 2025-03-14 00:00:00 | 2025-03-14 00:00:00 | N/A
CT3 | A1-3 | 2 | G1-S4464 | 1 | S-9 | 1 | DSA-250B | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A182 F304 | 304 | Pipe | Full coupling | BJC-G-8/8-158 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 | 2025-02-13 00:00:00 | ACC | - | - | - | Clear | CT3-TP-A1-3-002 | Seal air | 6.72 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A1-3 | 2 | G1-S4466 | 1 | S-18 | 1 | DIA-250A | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 | 2025-02-13 00:00:00 | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A1-3 | 2 | G1-S4467 | 1 | S-10 | 1 | DIA-251B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 | 2025-02-13 00:00:00 | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A1-3 | 2 | G1-S4467 | 1 | S-14 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 | 2025-02-13 00:00:00 | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A1-3 | 2 | G1-S4467 | 1 | S-29 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | 2025-02-13 00:00:00 | 2025-02-13 00:00:00 | ACC | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A1-3 | 2 | G1-S4474 | 1 | S-12 | 1 | DLOR-250A | BW | 1 | L | 10 | 3 | S40 | 9.27 | A106 Gr.B | A106 Gr.B | CS | Pipe | Pipe | BJC-G-1/1-154 | GTAW | 2025-01-29 00:00:00 | 2025-01-29 00:00:00 | 2025-01-29 00:00:00 | 2025-01-29 00:00:00 | - | - | ACC | - | Clear | CT3-TP-A1-3-003 | Lube oil return | 1.2 |  | 2025-02-01 00:00:00 | 2025-02-01 00:00:00
CT3 | A1-4 | 2 | G1-S4023 | 1 | S-5 | 2 | DFBA-275 | BW | 1 | S | 3 | 3 | S40 | 5.49 | A106 Gr.B | A234 WPB | CS | Pipe | Tee | BJC-G-1/1-154 | GTAW | 2025-03-04 00:00:00 | 2025-03-04 00:00:00 | 2025-03-04 00:00:00 | 2025-03-04 00:00:00 | - | - | ACC | - | Clear | CT3-TP-A1-4-001 | Filter bleed air | 1.2/33.6 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A3-3 | 2 | G1-S4506 | 1 | S-8 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | - | - | ACC | - | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | A3-3 | 2 | G1-S4506 | 1 | S-9 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | - | - | ACC | - | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | C2-1 | 2 | G1-S4010 | 1 | S-14 | 1 | DIA-525B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-02-13 00:00:00 | 2025-02-17 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | ACC | - | - | - | Clear | CT3-TP-C2-1-001 | Instrument air | 12 |  | 2025-04-05 00:00:00 | 2025-04-05 00:00:00
CT3 | D1-2 | 2 | G1-S4530 | 1 | seal weld 1 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-03-05 00:00:00 | 2025-03-05 00:00:00 | 2025-03-06 00:00:00 | 2025-03-07 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D1-2 | 2 | G1-S4530 | 1 | seal weld 2 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-03-05 00:00:00 | 2025-03-05 00:00:00 | 2025-03-06 00:00:00 | 2025-03-07 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D1-2 | 2 | G1-S4531 | 1 | S-6 | 2 | DSA-625 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-02-02 00:00:00 | 2025-02-02 00:00:00 | 2025-02-04 00:00:00 | 2025-02-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D1-2 | 2 | G1-S4531 | 1 | S-7 | 2 | DSA-625-1 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-02-02 00:00:00 | 2025-02-02 00:00:00 | 2025-02-04 00:00:00 | 2025-02-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D1-2 | 2 | G1-S4531 | 1 | S-15 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-02-02 00:00:00 | 2025-02-02 00:00:00 | 2025-02-04 00:00:00 | 2025-02-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D1-2 | 2 | G1-S4531 | 1 | S-16 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-02-02 00:00:00 | 2025-02-02 00:00:00 | 2025-02-04 00:00:00 | 2025-02-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-04-04 00:00:00 | 2025-04-04 00:00:00
CT3 | D2-1 | 2 | G1-S4087 | 1 | S-6 | 1 | DG-657A | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-1 | 2 | G1-S4087 | 1 | S-7 | 1 | DG-657B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | 2025-02-14 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4091 | 1 | S-1 | 4 | DG-675A | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-02-14 00:00:00 | 2025-02-15 00:00:00 | 2025-02-15 00:00:00 | 2025-02-15 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 1 | G1-S4091 | 1 | S-15 | 4 | DG-675A | FW | 8 | N/A | 10 | N/A | S80 | 12.70 | A312 TP304-S | A240 304 | 304 | Pipe | Plate | BJC-G-8/8-353 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4092 | 1 | S-10 | 3 | DG-676C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-15 00:00:00 | 2025-02-17 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4092 | 1 | S-16 | 3 | DG-676AB | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-02-14 00:00:00 | 2025-02-15 00:00:00 | 2025-02-15 00:00:00 | 2025-02-15 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4092 | 1 | S-6 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-02-10 00:00:00 | 2025-02-10 00:00:00 | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4092 | 1 | S-9 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-15 00:00:00 | 2025-02-17 00:00:00 | 2025-02-18 00:00:00 | 2025-02-18 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4094 | 1 | S-10 | 3 | DG-678B | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-02-10 00:00:00 | 2025-02-10 00:00:00 | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4094 | 1 | S-19 | 3 | DG-678C | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-02-10 00:00:00 | 2025-02-10 00:00:00 | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D2-2 | 2 | G1-S4094 | 1 | S-30 | 3 | DG-678D | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-02-10 00:00:00 | 2025-02-10 00:00:00 | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-04-08 00:00:00 | 2025-04-08 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | S-11 | 3 | DGSA-700AC | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | S-12 | 3 | DGSA-700B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-03-07 00:00:00 | 2025-03-11 00:00:00 | 2025-03-12 00:00:00 | 2025-03-13 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | S-4 | 3 | DGSA-700D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-26 00:00:00 | 2025-02-26 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | S-5 | 3 | DGSA-700C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-26 00:00:00 | 2025-02-26 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | seal weld 1 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-25 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | seal weld 2 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-25 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-1 | 2 | G1-S4100 | 1 | seal weld 3 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-25 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-10 | 5 | DFPA-710E | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-16 | 5 | DFPA-710BD | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-20 00:00:00 | 2025-02-21 00:00:00 | 2025-02-21 00:00:00 | 2025-02-21 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-17 | 5 | DFPA-710C | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-20 00:00:00 | 2025-02-21 00:00:00 | 2025-02-21 00:00:00 | 2025-02-21 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-3 | 5 | DFPA-710A | BW | 8 | S | 4 | 3 | S40 | 6.02 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-4 | 5 | DFPA-710D | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | 2025-02-20 00:00:00 | - | - | ACC | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | D3-2 | 2 | G1-S4104 | 1 | S-9 | 5 | DFPA-710D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-02-25 00:00:00 | 2025-02-25 00:00:00 | 2025-02-26 00:00:00 | 2025-02-27 00:00:00 | ACC | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-04-09 00:00:00 | 2025-04-09 00:00:00
CT3 | F1-2 | 2 | G1-S4546 | 1 | S15 | 2 | DGMB-750 | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Elbow 90 | BJC-G-8/8-158 | GTAW | 2025-02-10 00:00:00 | 2025-02-10 00:00:00 | 2025-02-11 00:00:00 | 2025-02-11 00:00:00 | ACC | - | - | - | Clear | [6 empty] | Modified Slope
CT3 | A1-3 | 3 | G1-S4466 |  | S-18 | 1 | DIA-250A | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-04-26 00:00:00 | 2025-05-03 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A1-3 | 3 | G1-S4467 |  | S-10 | 1 | DIA-251B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-05-23 00:00:00 | 2025-05-23 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A1-3 | 3 | G1-S4467 |  | S-14 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-05-23 00:00:00 | 2025-05-23 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A1-3 | 3 | G1-S4467 |  | S-29 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-04-26 00:00:00 | 2025-05-03 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A1-3 | 3 | G1-S4464 |  | S-9 | 1 | DSA-250B | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A182 F304 | 304 | Pipe | Full coupling | BJC-G-8/8-158 | GTAW | 2025-04-26 00:00:00 | 2025-05-03 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-002 | Seal air | 6.72 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A1-3 | 3 | G1-S4474 |  | S-12 | 1 | DLOR-250A | BW | 1 | L | 10 | 3 | S40 | 9.27 | A106 Gr.B | A106 Gr.B | CS | Pipe | Pipe | BJC-G-1/1-154 | GTAW | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-24 00:00:00 | 2025-03-25 00:00:00 | - |  | Acc |  | Clear | CT3-TP-A1-3-003 | Lube oil return | 1.2 |  | 2025-03-29 00:00:00 | 2025-03-29 00:00:00
CT3 | A1-4 | 3 | G1-S4023 |  | S-5 | 2 | DFBA-275-1 | BW | 1 | S | 3 | 3 | S40 | 5.49 | A106 Gr.B | A234 WPB | CS | Pipe | Tee | BJC-G-1/1-154 | GTAW | 2025-05-08 00:00:00 | 2025-05-08 00:00:00 | 2025-05-08 00:00:00 | 2025-05-08 00:00:00 | - |  | Acc |  | Clear | CT3-TP-A1-4-001 | Filter bleed air | 1.2/33.6 |  | 2025-05-31 00:00:00 | 2025-05-31 00:00:00
CT3 | A3-3 | 3 | G1-S4506 |  | S-8 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | - |  | Acc |  | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | A3-3 | 3 | G1-S4506 |  | S-9 | 2 | DGSA-400-1 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | 2025-05-02 00:00:00 | - |  | Acc |  | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | C2-1 | 3 | G1-S4010 |  | S-14 | 1 | DIA-525B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-04-22 00:00:00 | 2025-04-22 00:00:00 | 2025-04-23 00:00:00 | 2025-04-22 00:00:00 | Acc | - | - | - | Clear | CT3-TP-C2-1-001 | Instrument air | 12 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | D1-2 | 3 | G1-S4530 |  | seal weld 1 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-05-03 00:00:00 | 2025-05-03 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | Cancel | Cancel
CT3 | D1-2 | 3 | G1-S4530 |  | seal weld 2 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-05-03 00:00:00 | 2025-05-03 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | Cancel | Cancel
CT3 | D1-2 | 3 | G1-S4531 |  | S-15 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-09 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | D1-2 | 3 | G1-S4531 |  | S-16 | 2 | DSA-625-1 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-09 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | D1-2 | 3 | G1-S4531 |  | S-6 | 2 | DSA-625 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-09 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | D1-2 | 3 | G1-S4531 |  | S-7 | 2 | DSA-625-1 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-09 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-05-30 00:00:00 | 2025-05-30 00:00:00
CT3 | D2-1 | 3 | G1-S4087 |  | S-6 | 1 | DG-657A | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-1 | 3 | G1-S4087 |  | S-7 | 1 | DG-657B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | 2025-04-08 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4092 |  | S-10 | 3 | DG-676C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4092 |  | S-16 | 3 | DG-676AB | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-05 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4092 |  | S-6 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-07 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4092 |  | S-9 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4091 |  | S-1 | 4 | DG-675A | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-05 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 1 | G1-S4091 |  | S-15 | 4 | DG-675A | FW | 8 | N/A | 10 | N/A | S80 | 12.70 | A312 TP304-S | A240 304 | 304 | Pipe | Plate | BJC-G-8/8-353 | GTAW | 2025-05-23 00:00:00 | 2025-05-23 00:00:00 | 2025-05-28 00:00:00 | 2025-05-28 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | N/A | N/A
CT3 | D2-2 | 3 | G1-S4094 |  | S-10 | 3 | DG-678B | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-07 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4094 |  | S-19 | 3 | DG-678A | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-07 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D2-2 | 3 | G1-S4094 |  | S-30 | 3 | DG-678A | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-04-04 00:00:00 | 2025-04-04 00:00:00 | 2025-04-05 00:00:00 | 2025-04-07 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | S-11 | 3 | DGSA-700AC | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-25 00:00:00 | 2025-04-25 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | S-12 | 3 | DGSA-700B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-05-21 00:00:00 | 2025-05-22 00:00:00 | 2025-05-22 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | S-4 | 3 | DGSA-700D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-25 00:00:00 | 2025-04-25 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | S-5 | 3 | DGSA-700C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-24 00:00:00 | 2025-04-24 00:00:00 | 2025-04-25 00:00:00 | 2025-04-25 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | seal weld 1 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-05-22 00:00:00 | 2025-05-22 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | seal weld 2 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-05-22 00:00:00 | 2025-05-22 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-1 | 3 | G1-S4100 |  | seal weld 3 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-05-22 00:00:00 | 2025-05-22 00:00:00 | 2025-05-24 00:00:00 | 2025-05-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-10 | 5 | DFPA-710E | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-26 00:00:00 | 2025-04-26 00:00:00 | 2025-04-28 00:00:00 | 2025-04-28 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-16 | 5 | DFPA-710BD | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-22 00:00:00 | 2025-04-22 00:00:00 | 2025-04-23 00:00:00 | 2025-04-23 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-17 | 5 | DFPA-710C | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-22 00:00:00 | 2025-04-22 00:00:00 | 2025-04-23 00:00:00 | 2025-04-23 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-3 | 5 | DFPA-710A | BW | 8 | S | 4 | 3 | S40 | 6.02 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-04-22 00:00:00 | 2025-04-22 00:00:00 | 2025-04-23 00:00:00 | 2025-04-23 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-4 | 5 | DFPA-710D | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-22 00:00:00 | 2025-04-22 00:00:00 | 2025-04-23 00:00:00 | 2025-04-23 00:00:00 | - |  | Acc |  | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | D3-2 | 3 | G1-S4104 |  | S-9 | 5 | DFPA-710D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-04-26 00:00:00 | 2025-04-26 00:00:00 | 2025-04-28 00:00:00 | 2025-04-28 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-05-29 00:00:00 | 2025-05-29 00:00:00
CT3 | A1-3 | 4 | G1-S4466 |  | S-18 | 1 | DIA-250A | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-17 00:00:00 | 2025-07-17 00:00:00 | 2025-07-18 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A1-3 | 4 | G1-S4467 |  | S-10 | 1 | DIA-251B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-17 00:00:00 | 2025-07-17 00:00:00 | 2025-07-18 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A1-3 | 4 | G1-S4467 |  | S-14 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-17 00:00:00 | 2025-07-17 00:00:00 | 2025-07-18 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A1-3 | 4 | G1-S4467 |  | S-29 | 1 | DIA-251A | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-17 00:00:00 | 2025-07-17 00:00:00 | 2025-07-18 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-001 | Insument air | 12 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A1-3 | 4 | G1-S4464 |  | S-9 | 1 | DSA-250B | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A182 F304 | 304 | Pipe | Full coupling | BJC-G-8/8-158 | GTAW | 2025-07-17 00:00:00 | 2025-07-17 00:00:00 | 2025-07-18 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-A1-3-002 | Seal air | 6.72 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A1-3 | 4 | G1-S4474 |  | S-12 | 1 | DLOR-250A | BW | 1 | L | 10 | 3 | S40 | 9.27 | A106 Gr.B | A106 Gr.B | CS | Pipe | Pipe | BJC-G-1/1-154 | GTAW | 2025-05-29 00:00:00 | 2025-05-29 00:00:00 | 2025-05-29 00:00:00 | 2025-05-29 00:00:00 | - | - | Acc | - | Clear | CT3-TP-A1-3-003 | Lube oil return | 1.2 |  | 2025-06-14 00:00:00 | 2025-06-14 00:00:00
CT3 | A1-4 | 4 | G1-S4023 |  | S-5 | 2 | DFBA-275 | BW | 1 | S | 3 | 3 | S40 | 5.49 | A106 Gr.B | A234 WPB | CS | Pipe | Tee | BJC-G-1/1-154 | GTAW | 2025-07-15 00:00:00 | 2025-07-15 00:00:00 | 2025-07-16 00:00:00 | 2025-07-16 00:00:00 | - | - | Acc | - | Clear | CT3-TP-A1-4-001 | Filter bleed air | 1.2/33.6 |  | 2025-08-04 00:00:00 | 2025-08-04 00:00:00
CT3 | A3-3 | 4 | G1-S4506 |  | S-8 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-06-25 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | A3-3 | 4 | G1-S4506 |  | S-9 | 2 | DGSA-400 | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304H-S | A351 CF8 | 304H | Pipe | Valve | BJC-G-8/8-408 | GTAW | 2025-06-25 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-A3-3-001 | Fuel gas sweep air | 33.6 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | C2-1 | 4 | G1-S4010 |  | S-14 | 1 | DIA-525B | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-03 00:00:00 | 2025-07-03 00:00:00 | 2025-07-03 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-C2-1-001 | Instrument air | 12 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | D1-2 | 4 | G1-S4530 |  | seal weld 1 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-07-08 00:00:00 | 2025-07-08 00:00:00 | 2025-07-09 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | Cancel | Cancel
CT3 | D1-2 | 4 | G1-S4530 |  | seal weld 2 | 1 | DG-625 | FW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-07-08 00:00:00 | 2025-07-08 00:00:00 | 2025-07-09 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-001 | Fuel gas | 68.4 |  | Cancel | Cancel
CT3 | D1-2 | 4 | G1-S4531 |  | S-15 | 2 | DSA-625 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | 2025-06-21 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | D1-2 | 4 | G1-S4531 |  | S-16 | 2 | DSA-625 | SW | 8 | N/A | 1.5 | N/A | S40 | 3.68 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | 2025-06-21 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | D1-2 | 4 | G1-S4531 |  | S-6 | 2 | DSA-625 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | 2025-06-21 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | D1-2 | 4 | G1-S4531 |  | S-7 | 2 | DSA-625 | SW | 8 | N/A | 2 | N/A | S40 | 3.91 | A312 TP304-S | A216 WCB | Dissimilar | Pipe | Valve | BJC-G-1/8-163 | GTAW | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | 2025-06-21 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D1-2-002 | Seal air | 6.72/12 |  | 2025-08-02 00:00:00 | 2025-08-02 00:00:00
CT3 | D2-1 | 4 | G1-S4087 |  | S-6 | 1 | DG-657A | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-1 | 4 | G1-S4087 |  | S-7 | 1 | DG-657B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A312 TP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | 2025-06-20 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D2-1-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4092 |  | S-10 | 3 | DG-676C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-23 00:00:00 | 2025-06-23 00:00:00 | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4092 |  | S-16 | 3 | DG-676AB | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4092 |  | S-6 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | 2025-06-19 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4092 |  | S-9 | 3 | DG-676AB | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-23 00:00:00 | 2025-06-23 00:00:00 | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-001 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4091 |  | S-1 | 4 | DG-675A | BW | 8 | L | 10 | 3 | S80 | 12.70 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-353 | GTAW | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | 2025-06-19 00:00:00 | 2025-06-19 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 1 | G1-S4091 |  | S-15 | 4 | DG-675A | FW | 8 | N/A | 10 | N/A | S80 | 12.70 | A312 TP304-S | A240 304 | 304 | Pipe | Plate | BJC-G-8/8-353 | GTAW | 2025-06-23 00:00:00 | 2025-06-23 00:00:00 | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-002 | Fuel gas (DG) | 68.4 |  | N/A | N/A
CT3 | D2-2 | 4 | G1-S4094 |  | S-10 | 3 | DG-678B | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-06-14 00:00:00 | 2025-06-14 00:00:00 | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4094 |  | S-19 | 3 | DG-678C | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-06-14 00:00:00 | 2025-06-14 00:00:00 | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D2-2 | 4 | G1-S4094 |  | S-30 | 3 | DG-678D | SW | 8 | N/A | 0.75 | N/A | S40 | 2.87 | A312 TP304-S | A182 F304 | 304 | Pipe | Half coupling | BJC-G-8/8-158 | GTAW | 2025-06-14 00:00:00 | 2025-06-14 00:00:00 | 2025-06-18 00:00:00 | 2025-06-18 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D2-2-003 | Fuel gas (DG) | 68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | S-11 | 3 | DGSA-700A | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-06-30 00:00:00 | 2025-06-30 00:00:00 | 2025-06-30 00:00:00 | 2025-06-30 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | S-12 | 3 | DGSA-700B | BW | 8 | S | 3 | 3 | S40 | 5.49 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-07-22 00:00:00 | 2025-07-22 00:00:00 | 2025-07-22 00:00:00 | 2025-07-22 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | S-4 | 3 | DGSA-700D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-30 00:00:00 | 2025-06-30 00:00:00 | 2025-07-03 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | S-5 | 3 | DGSA-700C | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-30 00:00:00 | 2025-06-30 00:00:00 | 2025-07-03 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | seal weld 1 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | seal weld 2 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-1 | 4 | G1-S4100 |  | seal weld 3 | 3 | DGSA-700A | FW | 8 | N/A | 1 | N/A | S40 | 3.38 | A182 F304 | SUS316 | Dissimilar | Half coupling | Thermowell | BJC-G-8/8-156 | GTAW | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | 2025-08-01 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-1-001 | Fuel gas | 33.6/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-10 | 5 | DFPA-710E | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-07-04 00:00:00 | 2025-07-04 00:00:00 | 2025-07-05 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-16 | 5 | DFPA-710B | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-17 | 5 | DFPA-710C | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-3 | 5 | DFPA-710A | BW | 8 | S | 4 | 3 | S40 | 6.02 | A403 WP304-S | A351 CF8 | 304 | Reduce | Valve | BJC-G-8/8-158 | GTAW | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-4 | 5 | DFPA-710B | BW | 8 | S | 4 | 3 | S40 | 6.02 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-06-24 00:00:00 | 2025-06-24 00:00:00 | 2025-06-25 00:00:00 | 2025-06-26 00:00:00 | - | - | Acc | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | D3-2 | 4 | G1-S4104 |  | S-9 | 5 | DFPA-710D | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A351 CF8 | 304 | Pipe | Valve | BJC-G-8/8-158 | GTAW | 2025-07-04 00:00:00 | 2025-07-04 00:00:00 | 2025-07-05 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | 2025-08-05 00:00:00 | 2025-08-05 00:00:00
CT3 | F1-2 | 4 | G1-S4548 |  | S-3 | 2 | DGPB-750 | SW | 8 | N/A | 1 | N/A | S40 | 3.38 | A312 TP304-S | A182 F304 | 304 | Pipe | Tee | BJC-G-8/8-158 | GTAW | 2025-07-19 00:00:00 | 2025-07-19 00:00:00 | 2025-07-19 00:00:00 | 2025-07-21 00:00:00 | Acc | - | - | - | Clear | CT3-TP-D3-2-001 | GT fuel gas nozzle pure air | 12/68.4 |  | N/A | N/A | Modified