## Test_Packs
Project No | Project Name | Client | File Name | Test Package No | Module No | Unit | Piping System | Piping Name | Test Medium | Test Pressure | Design Pressure | Design Temp | Holding Time (min) | Stage | Status
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | Cedar-bayou Weld Map shop required.xlsx | Cedar-bayou Weld Map shop required | General | 1 | [7 empty] | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-FFS-1.xlsx | CT5-TP-FFS-1 | FFS | 1 | 64A0A | FIREFIGHTING SYSTEM PIPING | Nitrogen (N2) | 24.84 | 2.07 / 20.7 | 49 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-AC-FG-1.2-MBH01.xlsx | CT5-AC-FG-1.2-MBH01 | FG-1.2 | 1 | 24A0A | GT COMPRESSOR LOW/HIGH PRESSURE BLEED VALVE AIR CHAMBER PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-FG-1.2-1.xlsx | CT5-TP-FG-1.2-1 | FG-1.2 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-FG-2.2-1.xlsx | CT5-TP-FG-2.2-1 | FG-2.2 | 1 | 21A0H | FUEL GAS PIPING | Nitrogen (N2) | 70.8 | 5.90 / 59.0 | 300 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-AC-MD-1.1-MBH02.xlsx | CT5-AC-MD-1.2-MBH02 | MD-1.1 | 1 | 24A0A | GT COMPRESSOR MIDDLE PRESSURE BLEED VALVE AIR CHAMBER | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.1-1.xlsx | CT5-TP-MD-1.1-1 | MD-1.1 | 1 | 23A0H | SEAL AIR PIPING | Nitrogen (N2) | 6.72 | 0.56 / 5.6 | 310 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.1-2.xlsx | CT5-TP-MD-1.1-2 | MD-1.1 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.1-3.xlsx | CT5-TP-MD-1.1-3 | MD-1.1 | 1 | 27A0B | LUBE OIL RETURN PIPING | Nitrogen (N2) | 1.2 | 0.1 / 1.0 | 90 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.1-4.xlsx | CT5-TP-MD-1.1-4 | MD-1.1 | 1 | 45A0A | BLADE WASHING DRAIN PIPING | Nitrogen (N2) | See line list | See line list | See line list | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.2-1.xlsx | CT5-TP-MD-1.2-1 | MD-1.2 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.2-2.xlsx | CT4-TP-MD-1.2-2 | MD-1.2 | 1 | 21A0A | FUEL GAS MAIN A PIPING | Nitrogen (N2) | 70.8 | 5.9 / 59.0 | 300 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-1.2-3.xlsx | CT5-TP-MD-1.2-3 | MD-1.2 | 1 | 21A0C | FUEL GAS TOPHAT PIPING | Nitrogen (N2) | 70.8 | 5.90 / 59.0 | 300 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-2.1-1.xlsx | CT5-TP-MD-2.1-1 | MD-2.1 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-2.1-2.xlsx | CT5-TP-MD-2.1-2 | MD-2.1 | 1 | 27A0A | LUBE OIL SUPPLY PIPING | Nitrogen (N2) | 6 | 0.5 / 5.0 | 90 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-2.1-3.xlsx | CT5-TP-MD-2.1-3 | MD-2.1 | 1 | 27A0C | LUBE OIL VAPOR PIPING | Nitrogen (N2) | 6 | 0.05 / 0.5 | 90 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-2.2-1.xlsx | CT5-TP-MD-2.2-1 | MD-2.2 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-2.2-2.xlsx | CT5-TP-MD-2.2-2 | MD-2.2 | 1 | 21A0E | FUEL GAS PILOT B PIPING | Nitrogen (N2) | 70.8 | 5.90 / 59.0 | 300 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-3.2-1.xlsx | CT5-TP-MD-3.2-1 | MD-3.2 | 1 | 24A0A | INSTRUMENT AIR PIPING | Nitrogen (N2) | 12.36 | 1.03 / 10.3 | 60 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-3.2-2.xlsx | CT5-TP-MD-3.2-2 | MD-3.2 | 1 | 21A0H | FUEL GAS PIPING | Nitrogen (N2) | 70.8 | 5.90 / 59.0 | 300 | 10 | Pressure Test | Active
CT5 | NRG Cedar Bayou Project | CIMTAS (NINGBO) STEELPROCESSING.CO.,LTD. | CT5-TP-MD-3.2-3.xlsx | CT5-TP-MD-3.2-3 | MD-3.2 | 1 | 26A0A | NOZZLE SWEEP AIR PIPING | Nitrogen (N2) | 30.6 | 2.80 / 28.0 | 420 | 10 | Pressure Test | Active

## Drawings_ISO
Project No | Test Package No | Module No | Item No | Drawing No | Sheet | Rev | P&ID Reference
CT5 | CT5-TP-FFS-1 | FFS | 1 | - | 1 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 2 | - | 1 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 2 | - | 2 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 3 | - | 3 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 4 | - | 3 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 5 | - | 4 OF 6 | 2
CT5 | CT5-TP-FFS-1 | FFS | 6 | 4 OF 6 | 2 | FG-2.2
CT5 | CT5-TP-FFS-1 | FFS | 7 | 5 OF 6 | 2 | FG-2.2
CT5 | CT5-TP-FFS-1 | FFS | 8 | 5 OF 6 | 2 | FG-2.2
CT5 | CT5-TP-FFS-1 | FFS | 9 | 6 OF 6 | 2 | FG-2.2
CT5 | CT5-TP-FFS-1 | FFS | 10 | 6 OF 6 | 2 | FG-2.2
CT5 | CT5-TP-FFS-1 | FFS | 12 | 1 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 13 | 1 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 14 | 2 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 15 | 3 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 16 | 3 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 17 | 3 OF 3 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 18 | 1 OF 1 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 19 | 1 OF 15 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 20 | 2 OF 15 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 21 | 3 OF 15 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 22 | 4 OF 15 | 2 | -
CT5 | CT5-TP-FFS-1 | FFS | 23 | - | 5 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 24 | - | 5 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 25 | - | 6 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 26 | - | 6 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 27 | - | 7 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 28 | - | 8 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 29 | - | 8 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 30 | - | 10 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 31 | - | 12 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 32 | - | 13 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 33 | - | 13 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 34 | - | 14 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 35 | - | 14 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 36 | - | 14 OF 15 | 2
CT5 | CT5-TP-FFS-1 | FFS | 37 | - | 1 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 38 | - | 2 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 39 | - | 2 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 40 | - | 3 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 41 | - | 3 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 42 | - | 4 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 43 | - | 5 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 44 | - | 6 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 45 | - | 7 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 46 | - | 8 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 47 | - | 8 OF 9 | 2
CT5 | CT5-TP-FFS-1 | FFS | 48 | - | 1 OF 2 | 2
CT5 | CT5-TP-FFS-1 | FFS | 49 | - | 1 OF 2 | 2
CT5 | CT5-TP-FFS-1 | FFS | 50 | - | 2 OF 2 | 2
CT5 | CT5-TP-FFS-1 | FFS | 51 | - | 1 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 52 | - | 2 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 53 | - | 3 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 54 | - | 3 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 55 | - | 4 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 56 | - | 5 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 57 | - | 6 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 58 | - | 7 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 59 | - | 7 OF 7 | 2
CT5 | CT5-TP-FFS-1 | FFS | 60 | - | 1 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 61 | - | 2 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 62 | - | 3 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 63 | - | 4 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 64 | - | 4 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 65 | - | 5 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 66 | - | 7 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 67 | - | 7 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 68 | - | 8 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 69 | - | 8 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 70 | - | 10 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 71 | - | 11 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 72 | - | 13 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 73 | - | 13 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 74 | - | 14 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 75 | - | 15 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 76 | - | 16 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 77 | - | 17 OF 17 | 2
CT5 | CT5-TP-FFS-1 | FFS | 78 | - | 1 OF 2 | 2
CT5 | CT5-TP-FFS-1 | FFS | 79 | - | 1 OF 2 | 2
CT5 | CT5-TP-FFS-1 | FFS | 80 | - | 1 OF 2 | 2
CT5 | CT5-AC-FG-1.2-MBH01 | FG-1.2 | 1 | LM-02547 | 1 of 2 | 0
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 1 | LM-02547 | 4 OF 5 | 0
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 2 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 3 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 4 | LM-02547 | 3 OF 5 | 0
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 5 | LM-02547 | 1 OF 3 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 1 | LM-02531 | 4 OF 4 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 2 | LM-02525 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 3 | LM-02526 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 4 | LM-02527 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 5 | LM-02528 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 6 | LM-02529 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 7 | LM-02531 | 1 OF 2 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 8 | LM-02531 | 2 OF 4 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 9 | LM-02531 | 2 OF 2 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 10 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 11 | LM-02531 | 1 OF 4 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 12 | LM-02531 | 1 OF 2 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 13 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 14 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 15 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 16 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 17 | LM-02531 | 2 OF 2 | 0
CT5 | CT5-AC-MD-1.2-MBH02 | MD-1.1 | 1 | LM-02547 | 1 of 2 | 0
CT5 | CT5-TP-MD-1.1-1 | MD-1.1 | 1 | LM-02539 | 4 OF 8 | 0
CT5 | CT5-TP-MD-1.1-1 | MD-1.1 | 2 | LM-02539 | 3 OF 8 | 0
CT5 | CT5-TP-MD-1.1-1 | MD-1.1 | 3 | LM-02539 | 3 OF 8 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 1 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 2 | LM-02547 | 4 OF 4 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 3 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 4 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 5 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 6 | LM-02547 | 3 OF 4 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 7 | LM-02547 | 3 OF 4 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 8 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 9 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 10 | LM-02547 | 2 OF 4 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 11 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 12 | LM-02547 | 1 OF 3 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 13 | LM-02547 | 1 OF 4 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 14 | LM-02547 | 5 OF 6 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 15 | LM-02547 | 5 OF 6 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 16 | LM-02547 | 5 OF 6 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 17 | LM-02547 | 1 OF 2 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 18 | LM-02547 | 6 OF 6 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 19 | LM-02547 | 6 OF 6 | 0
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 20 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 1 | LM-02551 | 3 OF 4 | 0
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 2 | LM-02551 | 3 OF 4 | 0
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 4 | LM-02551 | 2 OF 4 | 0
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 5 | LM-02551 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 1 | LM-02565 | 3 OF 3 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 2 | LM-02563 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 3 | LM-02561 | 1 OF 5 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 4 | LM-02561 | 2 OF 5 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 5 | LM-02561 | 3 OF 5 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 6 | LM-02561 | 4 OF 5 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 7 | LM-02561 | 4 OF 5 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 8 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 9 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 10 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 11 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 12 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 13 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 14 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 15 | LM-02561 | 2 OF 2 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 16 | LM-02561 | 2 OF 2 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 17 | LM-02561 | 1 OF 2 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 18 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 19 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 20 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 21 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 22 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 23 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 24 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 25 | LM-02561 | 1 OF 1 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 1 | LM-02547 | 1 OF 2 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 2 | LM-02547 | 2 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 3 | LM-02547 | 2 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 4 | LM-02547 | 1 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 5 | LM-02547 | 1 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 6 | LM-02547 | 2 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 7 | LM-02547 | 2 OF 5 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 8 | LM-02547 | 3 OF 6 | 0
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 9 | LM-02547 | 3 OF 6 | 0
CT5 | CT4-TP-MD-1.2-2 | MD-1.2 | 1 | LM-02525 | 3 OF 6 | 0
CT5 | CT4-TP-MD-1.2-2 | MD-1.2 | 2 | LM-02525 | 3 OF 6 | 0
CT5 | CT4-TP-MD-1.2-2 | MD-1.2 | 3 | LM-02525 | 5 OF 6 | 0
CT5 | CT4-TP-MD-1.2-2 | MD-1.2 | 4 | LM-02525 | 6 OF 6 | 0
CT5 | CT5-TP-MD-1.2-3 | MD-1.2 | 1 | LM-02527 | 3 OF 6 | 0
CT5 | CT5-TP-MD-1.2-3 | MD-1.2 | 2 | LM-02527 | 3 OF 6 | 0
CT5 | CT5-TP-MD-1.2-3 | MD-1.2 | 3 | LM-02527 | 5 OF 6 | 0
CT5 | CT5-TP-MD-1.2-3 | MD-1.2 | 4 | LM-02527 | 5 OF 6 | 0
CT5 | CT5-TP-MD-2.1-1 | MD-2.1 | 1 | LM-02547 | 2 OF 3 | 0
CT5 | CT5-TP-MD-2.1-1 | MD-2.1 | 2 | LM-02547 | 1 OF 3 | 0
CT5 | CT5-TP-MD-2.1-2 | MD-2.1 | 1 | LM-02531 | 3 OF 5 | 0
CT5 | CT5-TP-MD-2.1-2 | MD-2.1 | 2 | LM-02531 | 3 OF 5 | 0
CT5 | CT5-TP-MD-2.1-3 | MD-2.1 | 1 | LM-02552 | 3 OF 4 | 0
CT5 | CT5-TP-MD-2.1-3 | MD-2.1 | 2 | LM-02552 | 3 OF 4 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 1 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 2 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 3 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 4 | LM-02547 | 1 OF 2 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 5 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 6 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 7 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 8 | LM-02547 | 1 OF 6 | 0
CT5 | CT5-TP-MD-2.2-2 | MD-2.2 | 1 | LM-02529 | 2 OF 5 | 0
CT5 | CT5-TP-MD-2.2-2 | MD-2.2 | 2 | LM-02529 | 2 OF 5 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 1 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 2 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 3 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 4 | LM-02547 | 3 OF 3 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 5 | LM-02547 | 2 OF 3 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 6 | LM-02547 | 2 OF 3 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 7 | LM-02547 | 2 OF 3 | 0
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 8 | LM-02547 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-2 | MD-3.2 | 1 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-2 | MD-3.2 | 2 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-3 | MD-3.2 | 1 | LM-02531 | 1 OF 1 | 0
CT5 | CT5-TP-MD-3.2-3 | MD-3.2 | 2 | LM-02531 | 1 OF 2 | 0
CT5 | CT5-TP-MD-3.2-3 | MD-3.2 | 3 | LM-02531 | 2 OF 2 | 0
CT5 | CT5-TP-MD-3.2-3 | MD-3.2 | 4 | LM-02531 | 1 OF 1 | 0

## Punch_Items
Project No | Test Package No | Module No | Item No | Drawing No | Deficiency Description | Category | Status | Discipline | Punch Stage
CT5 | CT5-TP-FFS-1 | FFS | 1 | 64A0B-PS-01 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 2 | 64A0B-PS-02 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 3 | 64A0B-PS-03 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 4 | 64A0B-PS-04 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 5 | 64A0B-PS-05 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 6 | 64A0B-PS-07 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 7 | 64A0B-PS-08 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 8 | 64A0B-PS-09 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 9 | 64A0B-PS-10 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 10 | 64A0B-PS-11 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 11 | 64A0B-PS-12 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 12 | 64A0B-PS-13 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 13 | 64A0B-PS-14 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 14 | 64A0B-PS-15 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 15 | 64A0B-PS-16 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 16 | 64A0B-PS-17 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 17 | 64A0B-PS-18 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 18 | 64A0B-PS-19 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 19 | 64A0B-PS-20 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 20 | 64A0B-PS-21 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 21 | 64A0B-PS-22 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 22 | 64A0B-PS-23 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 23 | 64A0B-PS-24 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 24 | 64A0B-PS-25 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 25 | 64A0B-PS-26 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 26 | 64A0B-PS-26 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 27 | 64A0B-PS-27 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 28 | 64A0B-PS-28 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 29 | 64A0B-PS-29 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 30 | 64A0B-PS-30 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 31 | 64A0B-PS-31 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 32 | 64A0B-PS-32 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 33 | 64A0B-PS-33 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 34 | 64A0B-PS-34 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FFS-1 | FFS | 35 | 64A0B-PS-35 | FFS Pipe support to be weld | B | CLOSED | Piping | Pressure Test
CT5 | CT5-AC-FG-1.2-MBH01 | FG-1.2 | 1 | LM-02967 | Pipe spool to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FG-1.2-1 | FG-1.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-FG-2.2-1 | FG-2.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-AC-MD-1.2-MBH02 | MD-1.1 | 1 | LM-02967 | Pipe spool to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-1 | MD-1.1 | 1 | LM-02959 | Joint 27 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-1 | MD-1.1 | 2 | 23A0H-6-1 | Temporary pipe support to be install | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-2 | MD-1.1 | 1 | LM-02967 | Joint 17,33,19,13 to be cleaning | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 1 | 27A0B-PS-02 | Pipe not sit on permanent pipe support | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 2 | 27A0B-PS-03 | Pipe not sit on permanent pipe support | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 3 | 27A0B-PS-04 | Pipe not sit on permanent pipe support | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-3 | MD-1.1 | 4 | 27A0B-4-1 | Temporary pipe support to be install | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.1-4 | MD-1.1 | 1 | LM-02977 | Spool 45A0A-39 to 23A0A-9 to be torque bolt | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.2-1 | MD-1.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT4-TP-MD-1.2-2 | MD-1.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-1.2-3 | MD-1.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.1-1 | MD-2.1 | 1 | LM-02967 | Joint 18 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.1-1 | MD-2.1 | 2 | 24A0A-83-1 | Temporary pipe support to be install | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.1-2 | MD-2.1 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.1-3 | MD-2.1 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.2-1 | MD-2.2 | 1 | LM-02967 | Joint 32,16 to be Clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-2.2-2 | MD-2.2 | 1 | LM-02967 | Joint 32,16 to be Clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-3.2-1 | MD-3.2 | 1 | LM-02967 | Joint 32,16 to be Clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-3.2-2 | MD-3.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test
CT5 | CT5-TP-MD-3.2-3 | MD-3.2 | 1 | LM-02967 | Joint 34,38,28,22 to be clean | B | CLOSED | Piping | Pressure Test